## Slide 1: Identification of a Drinking Water Softening Model using Machine Learning
Jake Jenden
Internship supervisor: Erwin Visser, MSc
University of Twente supervisor: Prof. Dr. H. Zwart
Study: MSc Systems and Control
6 January 2020
Jake Jenden

## Slide 2: Aim of Research
Identify a drinking water softening model using Machine Learning (ML)
Jake Jenden

## Slide 3: Research Questions
Is it possible to develop a model of the softening treatment process of a Water Treatment Plant using ML?
Is the data provided for this research adequate to develop a model using ML?
Jake Jenden

## Slide 4: Table of contents
Background Information about the Softening Process
Data Pre-Processing and Data Analysis
Machine Learning (ML)
  Neural Network (NN)
  eXtreme Gradient Boost (XGBoost)
Methods
ML Results
Results Discussion and Conclusions
Jake Jenden

## Slide 5: Background Information

## Slide 6: Drinking Water Treatment Plant (WTP)
Jake Jenden
Step 1:
Ozonation is carried out on the pre-treated water for disinfection of micro pollutants
Step 2:
Softening reactors are used to reduce the hardness of the water
Step 3:
Biological Activated Carbon (BAC) filters are used to remove organic matter and organic micro pollutants
Step 4:
A slow sand filter removes suspended solids
Step 5:
The resulting water is stored in a clear water reservoir ready for distribution

## Slide 7: Definition and Problems of Hard Water
Hardness is measured by adding the concentration of calcium and magnesium ions in water
More lead and copper is dissolved in the distributed water
A higher detergent dosage for washing is required for harder water
Scale buildup in heating equipment and appliances
Hard water tastes worse than soft water
Jake Jenden
Notes:   Ingestion of large quantities of copper and lead has negative effects on the public’s health
  Higher household costs
Increase in energy consumption
Equipment defects

## Slide 8: Pellet Softening Reactor
Jake Jenden
Calcium carbonate crystallisation on the seeding material leads to a variation of pellet sizes
Dosing heads in the circular plate, allow the water to pass through
Caustic soda is fed into the reactor via the pipe labeled B
Draining of the pellets occurs via tap C
Figure 1: Softening pellet reactor (L. Rietveld, 2015)
Notes: Water is pumped in an upward direction
Reactor is filled with seeding material
  Heavier larger pellets sink to a lower height in the reactor
  Lighter smaller pellets float higher in the reactor
  Facilitates the calcium carbonate crystallisation reaction
  An increase in pellet diameters leads to an increase pressure difference
  Once a particular pressure difference threshold is exceeded, the draining action is instigated

## Slide 9: Data Pre-Processing

## Slide 10: Corrupted Data
Dataset contains erroneous values, such as duplicated or missing values
  Often encoded as blanks, NaNs, null-values or other placeholders
Erroneous values in the dataset reduces the performance of ML algorithms
Often erroneous values in time series datasets
  Sensors for time series readings are often temporarily switched-off, damaged or blocked
  Therefore, missing values arise in the time series dataset
Jake Jenden

## Slide 11: Removing Corrupted Data Techniques
Remove the rows containing erroneous values
  Con: ML models learn from data with missing time steps
Interpolation of erroneous values
  Interpolation means estimating data values based on known sequential-data
Set the missing values to a constant number, e.g. 0 or a large negative value
  Idea is that the ML algorithm ignores the irregular values when training the model
The method adopted to tackle corrupted data, depends on the dataset
Jake Jenden

## Slide 12: Machine Learning (ML)

## Slide 13: Definition of Machine Learning (ML)
Informal definition:
  Machine Learning (ML) is the science of programming computers using algorithms, so they can learn from data
Formal definition:
  A computer program is said to learn from experience E with respect to some task T and some performance measure P, if its performance on T, as measured by P, improves with experience E
Jake Jenden

## Slide 14: Supervised Learning
Feed the ML algorithm with input-output training data pairs
ML algorithm generates a function (model) that maps the input to the output, i.e. Y=f(X)
Unsupervised learning is when the training data does not include an output to learn from
This research focusses only on supervised learning
Jake Jenden
Figure 2: Supervised learning example (A. Géron, 2017)

## Slide 15: ML Data Partitions and Hyperparameters
A hyperparameter is a parameter of a learning algorithm and external to the model
A dataset is often for ML partitioned into: train, validation and test datasets
Train partition is used for training during the implementation of the ML algorithm
Validation partition is used to evaluate the model during training
  Allows you to effectively tune the hyperparameters
Test partition consists of data used to determine the final performance of the created model
Jake Jenden

## Slide 16: Train-Validation-Test Data Split
Jake Jenden
Most often data splitting method used in ML
Train-validation-test data split, splits the whole dataset into train, validation and test partitions
A data split of 80% train data and 20% test data is often selected as a starting point
  A validation partition is not considered always necessary

## Slide 17: Walk-Forward Data Split
Jake Jenden
Originally designed by the financial trading industry
Data is split into windows
A model is generated for each set of windowed data
Helps to validate whether the hyperparameters need to be adjusted to improve performance during training
Notes: These days, often applied on time series datasets
Each window has the same train-test data split
Following window is the same length and shifted in time by the length of the test set

## Slide 18: Overfitting and Underfitting
Jake Jenden
Overfitting happens when a ML model fits the train dataset too closely
  Consequently, the random fluctuates in the training set are learnt as concepts in the model
  Therefore, not as effective at dealing with new data
Underfitting occurs when a ML model is unable to fit the training data nor new data (i.e. test dataset)
Figure 3: Overfitting example (A. Bhande, 2018)

## Slide 19: Neural Networks (NNs)

## Slide 20: Neural Networks (NNs) Introduction
Jake Jenden
Neural Networks (NNs) consist of layers of neurons with weights interlinking them
An example of a feedforward network, since connections are in a forward direction
Bias neurons are not dependent on previous layers
Key: Green circles = input neurons, orange circles = bias neurons, blue circles = hidden neurons

## Slide 21: Recurrent Neural Networks (RNNs)
Jake Jenden
A recurrent Neural Network (RNN) is a more complex version of a neural network
Connections can also go in a backwards directions
Uses previous outputs to calculate the current output
Key: X=input, Y=output
Notes: Line pointing to the next time step neuron represents the backwards direction

## Slide 22: Standard Time Series RNN Structure
Jake Jenden
Layers in an RNN often include LSTM cells and dropout layers
Optimum structure varies for each dataset
Structure adopted for this research is shown below

## Slide 23: Long Short-Term Memory (LSTM) Cells
Jake Jenden
LSTM cells selectively save information from previous outputs based on an algorithm
Aim is to prevent the vanishing gradient problem
The stored previous outputs are used to determine the current output
  Memory function used to calculate the output
Key: x=input, y=output, h=memory function

## Slide 24: Dropout Layer
Jake Jenden
Aim of a dropout layer is to reduce overfitting
At every training step, every neuron has probability p (e.g. p=50%) of not being used
Reduces co-dependencies in the network
Key: Orange circles = bias neurons, blue circles = hidden neurons, crosses = inactive neuron

## Slide 25: Gradient Descent
Jake Jenden
Gradient descent is an algorithm used to update the weights (parameters) in a NN
An iterative optimisation algorithm
A cost function is a measure of error between the actual data points and the prediction
Gradient is used to find the optimum point (optimum set of weights) that reduces the cost function

## Slide 26: eXtreme Gradient Boost (XGBoost)

## Slide 27: Introduction to Decision Trees
Jake Jenden
Definition of a decision tree (M. Rouse, 2012):
  A decision tree is a graph that uses a branching method to illustrate every possible outcome of a decision
Decisions are made using numeric ranges and if statements

## Slide 28: Introduction to XGBoost
Jake Jenden
eXtreme Gradient Boost (XGBoost) has won many prizes online
Algorithm was introduced in 2016 by T. Chen
An XGBoost model is a combination of decision tree models
The XGBoost model performs better than the best individual decision tree model
Figure 4: Continuous incorporation of new models (A. Géron, 2017)

## Slide 29: Model Prediction Horizons
Jake Jenden
Prediction time steps from the current time step to a certain future time step is called the horizon
XGBoost model does not make a prediction for future time steps
RNN has a horizon with future time steps
Key: F= forecast length, L=number of previous time steps

## Slide 30: Methods

## Slide 31: Identification of Inputs and Outputs
pH is chosen as output of model
  pH has good properties for control
Based on insight into the water softening treatment system, the following inputs are chosen:
  Caustic soda flow [m^3/h]
  Bottom Pressure [kPa] – pressure at bottom of reactor
  Pellet-bed pressure [kPa] – pressure difference across pellet-bed
  Bed Height [cm] – height of the pellet-bed
  Draining [-]
  Seeding [-]
Jake Jenden

## Slide 32: Data Collection
Jake Jenden
Interpolation is applied to the data between the recorded values by the water company
A data interval of one minute is selected
  Provides satisfactory retention of data
  Low computation times
Key: Red dot= recorded value, green dot= not recorded

## Slide 33: Data Pre-Processing: Data Removal
Jake Jenden
Flow rate is largely dependent on the caustic flow rate
Corrupted data rows are removed from the dataset
  Retention of about two thirds of the dataset
Key: Red plot= water flow rate, blue plot= caustic soda flow rate

## Slide 34
Jake Jenden

## Slide 35: Data Pre-Processing: Data Splitting
Only 10% test data considered necessary, due to many data samples
RNN train-validation-test model applies a 30% validation partition
  Monitor the performance of the algorithm during training
  RNN train-validation-test model takes longer to run in general
MSE and R-squared are selected as the evaluation metrics
  MSE is a measure of error
  R-squared value measures the fit
Jake Jenden
Data Splitting Method | XGBoost | RNN
Walk-Forward | 90% train, 10% test | 90% train, 10% test
Train-Validation-Test | 90% train, 10% test | 65% train, 30% validation, 5% test

## Slide 36: Prediction
Python code created by A. Sadad is adapted and used for ML implementation
TensorFlow is used as backend
Keras is used as frontend
RNN training is applied using the forecast lengths: F=1[min], 4[hr] and 24[hr]
  Tests the limits of the RNN algorithm
XGBoost is not able to forecast
Jake Jenden
Notes: TensorFlow use mathematical symbols to calculate the differential
Keras is UI package in Python that makes use of TensorFlow

## Slide 37: Machine Learning (ML) Results

## Slide 38: Train-Validation-Test RNN (with F=1[min]) Results
Jake Jenden
MSE is equal to 0.0004
  Relatively low
R-squared is equal to 0.9007
  Good fit
Slight lag in prediction
  Heavily dependent on the previous pH value
  Not a great prediction
Key: Red dot= actual data point, blue dot= predicted data point

## Slide 39: Walk-Forward RNN (with F=1[min]) Results
Jake Jenden
Two models displayed from the total six
Model 0 has an MSE of 0.0013 and an R-squared value of 0.6373
Model 4 has an MSE of 0.0017 and an R-squared of 0.3
Slight lag in prediction
  Heavily dependent on previous pH value
  Not a great prediction

## Slide 40: Walk-Forward RNN (with F=4[hr]) Results
Jake Jenden
Two models displayed from the total nine
Actual data has flatter profile than the prediction due to interpolation
Model 5 has an MSE of 0.0081 and an R-squared value of -1.5569
  MSE is relatively low, but R-squared performs badly
Model 1 has an MSE of 0.0017 and an R-squared value of -801.8891

## Slide 41: Walk-Forward XGBoost Results
Jake Jenden
One model displayed from the total seven
Model 2 has an MSE of 0.0049 and an R-squared value of -0.2389
  Low MSE, but a poor R-squared value

## Slide 42: Discussion
RNN models are not able to effectively predict the trend of the pH
  Could be due to interpolation of the actual data
In general, all models have a relatively low MSE value
XGBoost models do not perform as well as the RNN models
  XGBoost does not incorporate past pH values as a feature
Jake Jenden

## Slide 43: Conclusions
Is it possible to develop a model of the softening treatment process of a WTP using Machine Learning (ML)?
  It is possible to develop a model of the process with a relatively low MSE, but a poor R-squared value
Is the data provided for this research sufficient to develop a model using ML?
  Data is insufficient, since it is interpolated and lacks the detail to identify a model with a good fit
Jake Jenden

## Slide 44: Further Research
Gather more data to use in training of the ML algorithms
  More trends to learn from, thus potentially a better performing model
Test the model on another reactor in the same Water Treatment Plant (WTP)
  Validation of the model
Gather data that is not interpolated
  Provides more information to create a better performing model
Use more inputs for generation of model
  For instance, install a hardness sensor in the softening reactors
Jake Jenden